Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 071700 - BENTONITE WATERPROOFING

- GENERAL

      - SUMMARY

        - Section Includes:

          - Bentonite waterproofing.

          - Molded-sheet drainage panels.

          - Insulation.

      - ACTION SUBMITTALS

        - Product Data:  For each type of product indicated.

        - Shop Drawings:  Show installation details for interface with other work.

      - INFORMATIONAL SUBMITTALS

        - Material certificates.

        - Product test reports.

        - Sample warranty.

      - QUALITY ASSURANCE

        - Preinstallation Conference:  Conduct conference at Project site.

      - WARRANTY

        - Special Warranty:  Manufacturer's standard form in which manufacturer and Installer agree(s) to repair or replace components of bentonite waterproofing system that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

          - Warranty Period:  Five years from date of Substantial Completion.

- PRODUCTS

Retain paragraph below for waterproofing below-grade slabs and vertical walls where saltwater is present or ground water is contaminated.

      - COMPOSITE HDPE/BENTONITE MEMBRANE

Products in this article are used for waterproofing split-slab construction, backfilled concrete and masonry walls, and earth-covered structures.

Tremco Commercial Sealants & Waterproofing's "Deckseal" has transparent HDPE membrane.

        - Composite HDPE/Bentonite-Polymer Membrane:  Minimum 200-mil- (5-mm-) thick membrane consisting of HDPE geomembrane liner bonded to a layer of bentonite-polymer clay granules.

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - CETCO; Volclay Ultraseal SP.

          - Puncture Resistance:  75 lbf (334 N) according to ASTM D 4833.

          - Vapor Permeance:  0.005 perms according to ASTM E 96.

      - COMPOSITE GEOTEXTILE-HDPE/BENTONITE MEMBRANE

        - Geotextile/Bentonite-Polymer Waterproofing:  Minimum 250-mil- (6.4-mm-) thick membrane of bentonite-polymer clay granules between two layers of geotextile polypropylene fabric, one woven and one nonwoven, needle punched and heat fused together.

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - CETCO; Volclay Ultraseal BT.

          - Puncture Resistance:  75 lbf (334 N) according to ASTM D 4833.

          - Vapor Permeance:  0.005 perms according to ASTM E 96.

      - INSTALLATION ACCESSORIES

        - General:  Manufacturer's standard accessories recommended for intended use and compatible with bentonite waterproofing.

Retain one or both of first two paragraphs below for type of protection course if required.  Delete both if molded-sheet drainage panels or insulation drainage panels will replace protection course.  Verify acceptability of type of protection course with manufacturers.  Indicate locations, such as plaza deck and foundation walls, if more than one type of protection course is required.

First paragraph below describes CETCO's "Protection Mat 10V" geotextile protection course.

        - Geotextile Protection Course:  As recommended by waterproofing manufacturer.

Retain first paragraph below if molded-sheet drainage panel products are specified in another Section.

Retain one or both of first two paragraphs below if specifying drainage panels in this Section.  Retain first paragraph if specifying nonwoven-geotextile-faced drainage panels, usually for foundation walls.  Verify acceptability of type of drainage panel with manufacturers.  Indicate locations, such as plaza deck and foundation walls, if more than one type of drainage panel is required.

        - Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel: If indicated in the Architectural drawings provide a manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 (0.21-mm) sieve laminated to one side with or without a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of 9 to 15 gpm per foot (112 to 188 L/min. per m).

Retain first paragraph below if specifying woven-geotextile-faced drainage panels, usually for plaza decks.

Retain first paragraph below if board insulation is required over waterproofing and if board insulation forms the first layer beneath an insulation drainage panel.

Retain first paragraph below for unfaced insulation drainage panels for foundation wall applications.

- EXECUTION

      - INSTALLATION, GENERAL

        - Prepare substrates to be waterproofed, install waterproofing and accessories, and protect waterproofing from damage and wetting according to manufacturer's written instructions.

        - Install protection course before backfilling or placing overburden when recommended by waterproofing manufacturer.

      - COMPOSITE GEOTEXTILE-HDPE/BENTONITE MEMBRANE INSTALLATION

        - Install a continuous layer of waterproofing membrane with ends and edges lapped a minimum of 3 inches (75 mm).  Stagger end joints between membranes.  Seal joints with permanent seam tape.

Retain subparagraph below if substrate is subject to hydrostatic pressure of 33 feet of water column (100 kPa) or more.

      - MOLDED-SHEET DRAINAGE PANEL INSTALLATION

        - Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate.  Use adhesives or mechanical fasteners that do not penetrate waterproofing.  Lap edges and ends of geotextile to maintain continuity.  Protect installed molded-sheet drainage panels during subsequent construction.

END OF SECTION 071700