SECTION 07 2726 - FLUID-APPLIED MEMBRANE AIR BARRIERS

Maintain Section format, including the UH master spec designation and version date in bold in the center columns of the header and footer.  Complete the header and footer with Project information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Maintain Section format, including the UH master spec designation and version date in the center columns of the header and footer.  Complete the header and footer with Project-specific information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect.” Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete hidden text after this Section has been edited for the Project.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

        - The Contractor's attention is specifically directed, but not limited, to the following documents for additional requirements:

          - The current version of the Uniform General Conditions for Construction Contracts, State of Texas, available on the web site of the Texas Facilities Commission

          - The University of Houston’s Supplemental General Conditions and Special Conditions for Construction.

      - SUMMARY

        - Section includes fluid-applied, vapor-permeable membrane air barriers.

      - PREINSTALLATION MEETINGS

        - Preinstallation Conference:  Conduct conference at Project site.

      - ACTION SUBMITTALS

        - Product Data:  For each type of product.

Retain paragraph and associated subparagraphs below if Project is to be LEED v4 certified.

- B.	LEED Action Submittals (Projects authorized for LEED certification only):

          - Building Product Disclosure and Optimization:

            - Leadership Extraction Practices

              - Extended Producer Responsibility (EPR): Submit documentation indicating that manufacturers have a take back or recycling program for the product purchased.

              - Wood Products: Certified by Forest Stewardship Council or USGBC approved equivalent.

                - Chain-of-Custody Certificates: For certified wood products. Include statement of costs.

                - Chain-of-Custody Qualification Data: For manufacturer and vendor.

              - Provide details of biobased material per Sustainable Agriculture Network’s Sustainable Agriculture Standard or USDA certified biobased product. Indicate cost, location of extraction, manufacture, and purchase of material.

              - Recycled Content: For products having recycled content, indicate percentages by weight of post-consumer and pre-consumer recycled content.

                - Include statement indicating costs for each product having recycled content.

            - Sourcing of Raw Materials: For products that are required to comply with requirements for regional materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material.

              - Include statement indicating distance to Project, cost for each regional material and the fraction by weight that is considered regional.

              - Product Certificates: For materials manufactured within 100 miles of Project, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project and cost for each raw material.

          - Indoor Environmental Quality, Low Emitting Materials: Building Products must be tested and compliant with the California Department of Public-Health (CDPH) Standard Method V1.1-2010, using the applicable exposure scenario.

            - Paints, and Coatings: For wet applied on site products, include printed statement of VOC content, showing compliance with the applicable VOC limits of the California Air Resources Board (CARB) 2007, Suggested Control Measure (SCM) for Architectural Coatings, or the South Coast Air Quality Management District (SCAQMD) Rule 1113, effective June 3,-2011.

            - Adhesives and Sealants: For wet applied on site products, submit printed statement showing compliance with the applicable chemical content requirements of SCAQMD Rule 1168, effective July 1, 2005 and rule amendment date of January 7, 2005.

              - Product Data: For installation adhesives, indicating VOC content.

            - Alternative tests for VOC above include ASTM D2369-10; ISO 11890 part 1; ASTM D6886-03; or ISO 11890-2.

            - Methylene Chloride and perchloroethylene may not be added to paints, coating, adhesive or sealants.

            - Composite Wood: Submit documentation showing that wood used in the project has low formaldehyde emissions that meet the California Air Resources Board ATCM for formaldehyde requirements for ultra-low emitting formaldehyde (ULEF) resins or no added formaldehyde resins.

            - Provide General Emissions Evaluation certificates for adhesives, sealants showing compliance with California Department of Public Health v1.1 emissions testing or equivalent.

          - Laboratory Test Reports: For installation adhesives indicating compliance with requirements for low-emitting materials.

- C.	Shop Drawings:  For air-barrier assemblies.

          - Include details for through-wall flashings, substrate joints and cracks, counterflashing strips, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction.

          - Include details of interfaces with other materials that form part of air/water barrier.

      - INFORMATIONAL SUBMITTALS

        - Product certificates: From air/water barrier manufacturer, certifying compatibility of air/water barriers and accessory materials with Project materials that connect to or that come in contact with the barrier.

Retain paragraph and associated subparagraphs below if Project is to be LEED v4 certified.

- B.	LEED Informational Submittals:

          - Building Product Disclosure and Optimization - Sourcing of Raw Materials:

            - Raw Material Sources and Extraction Reporting: Submit Raw materials supplier corporate Sustainability Reports (CSRs); documenting responsible extraction; including extraction locations, long term ecologically responsible land use, commitment to reducing environmental harms from extraction and manufacturing processes, and a commitment to meeting applicable standards or programs that address responsible sourcing criteria

              - Submit manufacturers' self-declared reports

              - Submit third party verified corporate sustainability reports (CSR) using one of the following frameworks"

                - Global Reporting Initiative (GRI) Sustainability Report

                - Organization for Economic Co-operation and Development (OECD)

                - Guidelines for Multinational Enterprises

                - UN Global Compact

                - ISO 26000

                - USGBC approved program.

          - Building Product Disclosure and Optimization - Material Ingredients

            - Material Ingredient Optimization: Submit manufacturer's Environmental Product Declaration (EPD) or at least one of the following:

              - GreenScreen V1.2 Benchmark: Third party report prepared by a licensed GreenScreen List Translator, or a full GreenScreen Assessment.

              - Cradle to Cradle: Manufacturer's published literature for the product bearing the Cradle to Cradle logo.

              - International Alternative Compliance Path - REACH Optimization

              - Declare: Manufacturer's completed Product Declaration Form

              - Other programs approved by USGBC

            - Product Manufacturer Supply Chain Optimization: Submit documentation from manufacturers for products that go beyond material ingredient optimization as follows:

              - Are sourced from product manufacturers who engage in validated and robust safety, health, hazard, and risk programs which at a minimum document at least 99 percent (by weight) of the ingredients used to make the building product or building material, and

              - Are sourced from product manufacturers with independent third party verification of their supply chain that at a minimum verifies:

                - Processes are in place to communicate and transparently prioritize chemical ingredients along the supply chain according to available hazard, exposure and use information to identify those that require more detailed evaluation

                - Processes are in place to identify, document, and communicate information on health, safety and environmental characteristics of chemical ingredients

                - Processes are in place to implement measures to manage the health, safety and environmental hazard and risk of chemical ingredients

                - Processes are in place to optimize health, safety and environmental impacts when designing and improving chemical ingredients

                - Processes are in place to communicate, receive and evaluate chemical ingredient safety and stewardship information along the supply chain

                - Safety and stewardship information about the chemical ingredients is publicly available from all points along the supply chain.

- C.	Product Test Reports.

      - QUALITY ASSURANCE

        - Installer Qualifications:  An entity that employs installers and supervisors who are trained and approved by manufacturer.

        - Mockups:  Build mockups to establish quality standards for materials and execution.

          - Build integrated mockups of exterior wall assembly as shown on Drawings, incorporating backup wall construction, external cladding, window, storefront, door frame and sill, insulation, ties and other penetrations, and flashing to demonstrate surface preparation, crack and joint treatment, application of air barriers, and sealing of gaps, terminations, and penetrations of air-barrier assembly.

            - Coordinate construction of mockups to permit inspection by Owner's testing agency of air barrier before external insulation and cladding are installed.

            - Include junction with roofing membrane and foundation wall intersection.

          - Mockup Testing: Air-barrier assemblies shall comply with performance requirements indicated, as evidenced by reports based on mockup testing by a qualified testing agency.

            - Adhesion Testing: Mockups will be tested for minimum air-barrier adhesion of 30 pounds/sq in. according to ASTM D 4541.

            - Notify Architect at least seven days in advance of the dates and times when mockups will be tested.

      - WARRANTY

        - Provide manufacturer’s standard 10-year material warranty.

      - DELIVERY, STORAGE, AND HANDLING

        - Store liquid materials in their original undamaged packages in a clean, dry, protected location and within temperature range required by air/water barrier manufacturer.

        - Remove and replace liquid materials that cannot be applied within their stated shelf life.

        - Protect stored materials from direct sunlight.

      - FIELD CONDITIONS

        - Environmental Limitations: Apply air/water barrier within the range of ambient and substrate temperatures recommended by air-barrier manufacturer.

          - Protect substrates from environmental conditions that affect air/water barrier performance.

        - Do not apply air/water barrier to a damp or wet substrate or during snow, rain, fog, or mist.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

Retain one of first two options in "General" Paragraph below depending on whether a vapor-retarding or -permeable air barrier is required.  Consider retaining third option if air barrier serves as a primary or secondary drainage plane.

        - General:  Air barrier shall be capable of performing as a continuous vapor-permeable air barrier and as a liquid-water drainage plane flashed to discharge to the exterior incidental condensation or water penetration.  Air-barrier assemblies shall be capable of accommodating substrate movement and of sealing substrate expansion and control joints, construction material changes, penetrations, and transitions at perimeter conditions without deterioration and air leakage exceeding specified limits.

        - Air/water barrier assembly shall be capable of resisting water penetration when tested according to ASTM E 1105 with a static air pressure differential of 6.24 psf for a period of one hour.

        - Air-Barrier Assembly Air Leakage: Maximum 0.04 cfm/sq. ft. of surface area at 1.57 lbf/sq. ft. (0.2 L/s x sq. m of surface area at 75 Pa), when tested according to ASTM E 2357.

      - VAPOR-PERMEABLE MEMBRANE AIR/WATER BARRIER, UV RESISTANT

        - Fluid-Applied, Vapor-Permeable Membrane Air/water Barrier:  Synthetic polymer membrane.

          - Products: Subject to compliance with requirements, provide one of the following:

            - Synthetic Polymer Membrane:

              - Henry Company: Air-Bloc 31.

              - W.R. Grace: Perm-A-Barrier VP.

              - Tremco: ExoAir 230.

          - Physical and Performance Properties:

            - Air Permeance: Maximum 0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft. (0.02 L/s x sq. m of surface area at 75-Pa) pressure difference; ASTM E 2178.

            - Vapor Permeance: Minimum 10 perms (580 ng/Pa x s x sq. m); ASTM E 96/E 96M.

            - Ultimate Elongation: Minimum 300 percent; ASTM D 412, Die C.

      - ACCESSORY MATERIALS

        - General:  Accessory materials recommended by air-barrier manufacturer to produce a complete air-barrier assembly and compatible with primary air-barrier material.

        - Sealant:   ASTM C 920, single-component, neutral-curing silicone; Class 100/50 (low modulus), Grade NS, Use NT related to exposure, and, as applicable to joint substrates indicated, Use O.

        - Termination Mastic:  Air-barrier manufacturer's standard cold fluid-applied elastomeric liquid; trowel grade or low viscosity.

          - Grace Construction Products: Bituthene Liquid Membrane.

        - Primers: Water based, low VOC as provided by the manufacturer.

        - Transition Flashing: 40 mil SBS modified bitumen self-adhering membrane with a cross-laminated polyethylene film for window and door sill flashing, door openings, inside and outside corners and other transitions as provided by the manufacturer.

          - Grace Construction Products: Perm-A-Barrier Detail Membrane.

          - Henry:  Blueskin SA.

        - Foil-Faced Self-Adhering Flashing: Modified bituminous, 40-mil thick, self-adhering sheet consisting of rubberized asphalt laminated to an aluminum-faced cross-laminated polyethylene film with release liner backing.

          - Grace Construction Products: Perm-A-Barrier Aluminum Flashing.

          - Henry: HE200AM Metal Clad Weather Barrier.

        - High-Temperature Self-Adhering flashing: Modified bituminous, 40-mil thick, self-adhering sheet consisting oof rubberized asphalt laminated to a cross-laminated polyethylene film with release liner backing, stable at temperature of 240 degrees F minimum.

          - Grace Construction Products: Ice and Water Shield HT.

          - Henry: Blueskin SA HT.

        - Joint Reinforcing Strip: Air/water barrier manufacturer’s glass-fiber-mesh tape.

        - Substrate-Patching Membrane: Air/water barrier manufacturer’s standard trowel-grade substrate filler.

        - Adhesive and Tape: Air/water barrier manufacturer’s standard adhesive and pressure-sensitive adhesive tape.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with installer present, for compliance with requirements and other conditions affecting performance of the Work.

          - Verify that substrates are sound and free of oil, grease, dirt, excess mortar, or other contaminants.

          - Verify that concrete has cured and aged for minimum time period recommended by air/water barrier manufacturer.

          - Verify that concrete is visibly dry and free of moisture. Test for moisture by capillary sheet method according to ASTM D 4263.

          - Verify that masonry surfaces are parge-coated and smooth.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - SURFACE PREPARATION

        - Clean, prepare, treat, and seal substrate according to manufacturer’s written instructions. Provide clean, dust-free, and dry substrate for air/water barrier application.

        - Mask off adjoining surfaces not covered by air barrier to prevent spillage and overspray affecting other construction.

        - Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids in concrete with substrate-patching membrane.

        - Remove excess mortar from masonry ties, shelf angles, and other obstructions.

        - At changes in substrate plane, apply sealant or termination mastic beads at sharp corners and edges to form a smooth transition from one plane to another.

      - INSTALLATION

Revise this article to coordinate with drawing details.  Place sheet or liquid-seal materials over a firm backing to provide structural support for achieving an effective and permanent air barrier.

        - General:  Install fluid-applied membrane air-barrier using spray equipment and accessory materials according to air-barrier manufacturer's written instructions to form a seal with adjacent construction and maintain a continuous air barrier.

          - Coordinate the installation of air barrier with installation of roofing membrane and base flashing to ensure continuity of air barrier with roofing membrane.

          - Install air-barrier assembly on roofing membrane or base flashing so that a minimum of 3 inches (75 mm) of coverage is achieved over each substrate.

          - Sequence Work so that detailing of self-adhered membrane flashing is completed prior to the installation of the fluid applied membrane.

        - Apply fluid air/water barrier material to form a seal with strips and transition strips and to achieve a continuous air/water barrier according to air/water barrier manufacturer’s written instructions. Apply fluid air-barrier material within manufacturer’s recommended application temperature ranges

        - Apply primer to substrates at required rate and allow it to dry.  Limit priming to areas that will be covered by fluid air-barrier material on same day.  Reprime areas exposed for more than 24 hours.

Retain subparagraph below if using glass-fiber-surfaced gypsum sheathing.

          - Prime glass-fiber-surfaced gypsum sheathing with number of prime coats needed to achieve required bond, with adequate drying time between coats.

        - Joint and Fastener Treatments:

          - Seal joints ¼ inch and less between panels of exterior grade gypsum, DensGlass Gold, plywood, OSB, or cementitious panels with joint treatment sealant.

          - Seal gaps and voids or irregular joints greater than ¼ inch between panels of exterior grade gypsum, DensGlass Gold, plywood, OSB or cementitious panels with a strip of self-adhering air/vapor barrier transition membrane lapped a minimum of 1 1/2 inches on both sides of the joint, according to ASTM C 1193 and air-barrier manufacturer’s written instructions

          - Provide joint treatment over heads of all sheathing fasteners.

        - Connect and seal exterior wall air-barrier material continuously to roofing-membrane air barrier, concrete below-grade structures, floor-to-floor construction, exterior glazing and window systems, glazed curtain-wall systems, storefront systems, exterior louvers, exterior door framing, and other construction used in exterior wall openings, using accessory materials.

        - At end of each working day, seal top edge of air barrier to substrate with termination mastic.

        - Wall Openings:  Prime concealed, perimeter frame surfaces of windows, curtain walls, storefronts, and doors.  Apply transitions and flashing so that a minimum of 3 inches (75 mm) of coverage is achieved over each substrate.  Maintain 3 inches (75 mm) of full contact over firm bearing to perimeter frames with not less than 1 inch (25 mm) of full contact.

        - Seal air-barrier assembly around masonry reinforcing or ties and penetrations with termination mastic.

        - Seal top of through-wall flashings to air barrier.

        - Seal exposed edges of strips at seams, cuts, penetrations, and terminations not concealed by metal counterflashings or ending in reglets with termination mastic.

        - Repair punctures, voids, and deficient lapped seams.  Slit and flatten fishmouths and blisters.  Extend patches 6 inches (150 mm) beyond repaired areas.

        - Fluid-Applied Membrane Material:  Apply a continuous unbroken air-barrier membrane to substrates according to the following thickness.  Apply air-barrier membrane in full contact around protrusions such as masonry ties.

          - Vapor-Permeable Membrane Air Barrier:  Total 45-mil (1.1-mm) dry film thickness, applied in one or more equal coats with spray equipment recommended by the manufacturer.

          - Apply self-adhering flashing strips over cured air/water barrier membrane according to air/water barrier manufacturer’s written instructions.

        - Do not cover air barrier until it has been tested and inspected by Owner's testing agency.

        - Correct deficiencies in or remove air barrier that does not comply with requirements; repair substrates and reapply air-barrier components.

      - FIELD QUALITY CONTROL

Coordinate test and inspection requirements in this article with Owner's testing agency.

        - Testing Agency:  Owner will engage a qualified testing agency to perform tests and inspections.

        - Inspections:  Air-barrier materials, accessories, and installation are subject to inspection for compliance with requirements.

          - Continuity of air/water barrier system has been achieved throughout the building envelope with no gaps or holes.

          - Continuous structural support of air/water barrier system has been provided.

          - Masonry and concrete surfaces are smooth, clean, and free of cavities, protrusions, and mortar droppings.

          - Site conditions for application temperature and dryness of substrates have been maintained.

          - Maximum exposure time of materials to UV deterioration has not been exceeded.

          - Surfaces have been primed, if applicable.

          - Laps in self-adhering flashing strips have complied with minimum requirements and have been shingled in the correct direction (or liquid membrane has been applied on exposed edges), with no fishmouths.

          - Liquid membrane has been applied on cut edges.

          - Self-adhering flashings have been firmly adhered to substrate.

          - Compatible materials have been used.

          - Transitions at changes in direction and structural support at gaps have been provided.

          - Connections between assemblies (air/water barrier and sealants) have complied with requirements for cleanliness, surface preparation and priming, structural support, integrity, and continuity of seal.

          - All penetrations have been sealed.

        - Tests:  As determined by Owner's testing agency from among the following tests:

          - Quantitative Air-Leakage Testing:  Air-barrier assemblies will be tested for air leakage according to ASTM E 783.

          - Adhesion Testing:  Air-barrier assemblies will be tested for minimum air-barrier adhesion of 30 lbf/sq. in. (207 kPa) according to ASTM D 4541 for each 600 sq. ft. (56 sq. m) of installed air barrier or part thereof.

        - Air barriers will be considered defective if they do not pass tests and inspections.

          - Apply additional air-barrier material, according to manufacturer's written instructions, where inspection results indicate insufficient thickness.

          - Remove and replace deficient air-barrier components for retesting as specified above.

        - Repair damage to air barriers caused by testing; follow manufacturer's written instructions.

        - Remove and replace deficient air/water barrier components.

        - Protect air-barrier system from damage during application and remainder of construction period, according to manufacturer's written instructions.

          - Protect air barrier from exposure to UV light and harmful weather exposure as required by manufacturer.

          - If exposed to these conditions for more than 60 days, remove and replace air barrier or install additional, full-thickness, air-barrier application after repairing and preparing the overexposed membrane according to air-barrier manufacturer's written instructions.

          - Protect air barrier from contact with incompatible materials and sealants not approved by air-barrier manufacturer.

        - Clean spills, stains, and soiling from construction that would be exposed in the completed work using cleaning agents and procedures recommended by manufacturer of affected construction.

        - Remove masking materials after installation.

END OF SECTION 07 2726