Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 10 26 00 - WALL AND DOOR PROTECTION

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Wall guards.

          - Corner guards.

          - Impact-resistant wall coverings.

          - Door protection systems.

        - Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 05 50 00 "Metal Fabrications" for [metal angle corner guards] [pipe guards] [wheel guards].

          - Section 08 71 00 "Door Hardware" for metal armor, kick, mop, and push plates.

      - PERFORMANCE REQUIREMENTS

Requirements in this article are examples only and are based on typical requirements of model codes.  For some occupancy categories under certain circumstances, model codes have less-stringent provisions; revise to suit Project and to comply with requirements of authorities having jurisdiction.  Verify, with manufacturers, that their impact-resistant handrails can comply.

        - Structural Performance:  Provide handrails capable of withstanding the effects of gravity loads and the following loads and stresses within limits and under conditions indicated:

          - Uniform load of 50 lbf/ft. (0.73 kN/m) applied in any direction.

          - Concentrated load of 200 lbf (0.89 kN) applied in any direction.

          - Uniform and concentrated loads need not be assumed to act concurrently.

      - ACTION SUBMITTALS

        - Product Data:  Include construction details, material descriptions, impact strength[, fire-test-response characteristics], dimensions of individual components and profiles, and finishes for each impact-resistant wall protection unit.

        - LEED Submittals (Projects authorized for LEED certification only)

First option in "Certificates for (Credit MR 6) (Credit MR 7)" Subparagraph below applies to LEED-CS; second applies to LEED-NC, LEED-CI, and LEED for Schools.

          - Certificates for [Credit MR 6] [Credit MR 7]:  Chain-of-custody certificates certifying that wood rails comply with forest certification requirements.  Include evidence that manufacturer is certified for chain of custody by an FSC-accredited certification body.  Include statement indicating cost for each certified wood product.

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements selected in Part 2 for adhesives.

          - Product Data for Credit IEQ 4.1:  For adhesives, documentation including printed statement of VOC content.

"Product Data for Credit IEQ 4.4" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS.

          - Product Data for Credit IEQ 4.4:  For particleboard, documentation indicating that products contain no urea formaldehyde.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

          - Laboratory Test Reports for Credit IEQ 4:  For [adhesives] [and] [composite wood products], documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

        - Shop Drawings:  For each impact-resistant wall protection unit showing locations and extent.  Include sections, details, and attachments to other work.

Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify product's compliance with performance requirements.  Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

          - For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

        - Samples for Initial Selection:  For each type of impact-resistant wall protection unit indicated.

          - Include similar Samples of accent strips and accessories involving color selection.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain paragraph below with or without above.

        - Samples for Verification:  For each type of exposed finish required, prepared on Samples of size indicated below.[  Include Samples of accent strips to verify color selected.]

          - [Wall] [and] [Corner] Guards:  12 inches (300 mm) long.  Include examples of joinery, corners, [end caps,] [top caps,] and field splices.

          - Handrails:  12 inches (300 mm) long.  Include examples of joinery, corners, and field splices.

          - Impact-Resistant Wall Covering:  6 by 6 inches (150 by 150 mm) square.

          - Door-Surface Protection:  6 by 6 inches (150 by 150 mm) square.

          - Door[-Edge] [and] [-Frame] Protectors:  12 inches (300 mm) long.

          - Door-Knob and -Lever Protectors:  Full-size unit of each type.

      - INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data:  For qualified [Installer] [testing agency].

Retain first paragraph below for material certificates from manufacturers.

        - Material Certificates:  For each impact-resistant plastic material, from manufacturer.

Retain first paragraph below for material test reports that are Contractor's responsibility.

        - Material Test Reports:  For each impact-resistant plastic material.

        - Warranty:  Sample of special warranty.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data:  For each impact-resistant wall protection unit to include in maintenance manuals.

          - Include recommended methods and frequency of maintenance for maintaining optimum condition of plastic covers under anticipated traffic and use conditions.  Include precautions against using cleaning materials and methods that may be detrimental to plastic finishes and performance.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - [Wall-Guard] [and] [Handrail] Covers:  Full-size plastic covers of maximum length equal to [2] <Insert number> percent of each type, color, and texture of units installed, but no fewer than [two, 8-foot- (2.4-m-)] <Insert number and size> long units.

          - Corner-Guard Covers:  Full-size plastic covers of maximum length equal to [2] <Insert number> percent of each type, color, and texture of units installed, but no fewer than [two, 4-foot- (1.2-m-)] <Insert number and size> long units.

        - Include mounting and accessory components.  Replacement materials shall be from same production run as installed units.

      - QUALITY ASSURANCE

        - Installer Qualifications:  An employer of workers trained and approved by manufacturer.

        - Source Limitations:  Obtain impact-resistant wall protection units from single source from single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.

        - Product Options:  Drawings indicate size, profiles, and dimensional requirements of impact-resistant wall protection units and are based on the specific system indicated.  Refer to Section 01 40 00 "Quality Requirements."

        - Revise subparagraph below to suit Project.

          - Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

        - Surface-Burning Characteristics:  Provide impact-resistant, plastic wall protection units with surface-burning characteristics as determined by testing identical products per ASTM E 84, NFPA 255, or UL 723 by UL or another qualified testing agency.

Retain first paragraph below for compliance of handrails and wall guards with accessible design criteria and protrusion limitations.

        - Regulatory Requirements:  Comply with applicable provisions in [the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines] [and] [ICC/ANSI A117.1].

Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

        - Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

      - DELIVERY, STORAGE, AND HANDLING

        - Store impact-resistant wall protection units in original undamaged packages and containers inside well-ventilated area protected from weather, moisture, soiling, extreme temperatures, and humidity.

          - Maintain room temperature within storage area at not less than 70 deg F (21 deg C) during the period plastic materials are stored.

          - Keep plastic sheet material out of direct sunlight.

          - Store plastic wall protection components for a minimum of 72 hours, or until plastic material attains a minimum room temperature of 70 deg F (21 deg C).

            - Store corner-guard covers in a vertical position.

            - Store [wall-guard] [bed-locator] [and] [handrail] covers in a horizontal position.

      - PROJECT CONDITIONS

        - Environmental Limitations:  Do not deliver or install impact-resistant wall protection units until building is enclosed and weatherproof, wet work is complete and dry, and HVAC system is operating and maintaining temperature at 70 deg F (21 deg C) for not less than 72 hours before beginning installation and for the remainder of the construction period.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of impact-resistant wall protection units that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Structural failures.

            - Deterioration of plastic and other materials beyond normal use.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

          - Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

- PRODUCTS

      - MATERIALS

Retain materials in this article that correspond with products retained in other Part 2 articles.

Revise impact resistance in first two paragraphs below to suit Project.  Value of 25.4 ft-lbf/in. (1356 J/m) of notch is an acceptable minimum for rigid vinyl plastic products.  See Evaluations for discussion on other impact-resistance test methods used by some manufacturers.

        - PVC Plastic:  ASTM D 1784, Class 1, textured, chemical- and stain-resistant, high-impact-resistant PVC or acrylic-modified vinyl plastic with integral color throughout; extruded and sheet material, thickness as indicated.

Although option in first subparagraph below is typical, not all listed manufacturers provide any products or an entire product line that can achieve 25.4 ft-lbf/in. (1356 J/m) of notch when tested according to ASTM D 256, Test Method A.  Consult manufacturers.

          - Impact Resistance:  Minimum 25.4 ft-lbf/in. (1356 J/m)  of notch when tested according to ASTM D 256, Test Method A.

          - Self-extinguishing when tested according to ASTM D 635.

          - Flame-Spread Index:  25 or less.

          - Smoke-Developed Index:  450 or less.

        - Polycarbonate Plastic Sheet:  ASTM D 6098, S-PC01, Class 1 or 2, abrasion resistant; with a minimum impact-resistance rating of 15 ft-lbf/in. (800 J/m) of notch when tested according to ASTM D 256, Test Method A.

        - Aluminum Extrusions:  Alloy and temper recommended by manufacturer for type of use and finish indicated, but with not less than strength and durability properties specified in ASTM B 221 (ASTM B 221M) for Alloy 6063-T5.

        - Stainless-Steel Sheet:  ASTM A 240/A 240M.

        - Brass:  ASTM B 249/B 249M for extruded shapes and ASTM B 36/B 36 M for sheet.

        - Solid Wood:  Clear hardwood lumber of species indicated, free of appearance defects, and selected for compatible grain and color.

Retain second option in "Particleboard" Paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.4.  Retain third option if required for LEED for Schools Credit IEQ 4.

        - Particleboard:  Not allowed.

        - Adhesive:  As recommended by impact-resistant plastic wall protection manufacturer.

Copy paragraphs in first six articles below and re-edit for each product.

Insert number to complete drawing designation for each product required.  Use these designations on Drawings to identify each product.

      - WALL GUARDS

See Evaluations for discussion on types of wall guards.

        - Crash Rail :  Heavy-duty assembly consisting of continuous snap-on plastic cover installed over concealed retainer system; designed to withstand impacts.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following :

          - Basis-of-Design Product:  Subject to compliance with requirements, provide    comparable product by one of the following:

            - IPC Door and Wall Protection Systems; Division of InPro Corporation.

            - Korogard Wall Protection Systems; a division of RJF International Corporation.

            - Substitutions:  See Section 01 25 00 – Substitution Procedures.

Revise description in first subparagraph below to suit product and Project.

          - Cover:  Extruded rigid plastic, minimum 0.100-inch (2.5-mm) wall thickness; as follows:

            - Profile:  Flat  .

              - Dimensions:  Nominal 6 inches high by 1 inch deep (150 mm high by 25 mm deep)  .

              - Surface:  Uniform   .

Retain first subparagraph below if required.  Revise last subparagraph above and subparagraph below if more than one accent inlay strip is required to suit product.

            - Color and Texture:    As selected by Architect from manufacturer's full range .

Retain one of first two subparagraphs below to suit product and performance level required to suit Project.  First subparagraph is typical, revise if continuous retainer is galvanized steel or plastic rather than aluminum, or if another retainer system is required.

          - Continuous Retainer:  Minimum 0.080-inch- (2.0-mm-) thick, one-piece, extruded aluminum.

          - Retainer Clips:  Manufacturer's standard impact-absorbing clips designed for heavy-duty performance.

Retain first subparagraph below to suit product or if required for increased impact absorption when mounting rail.

          - Bumper:  Continuous rubber or vinyl bumper cushion(s).

Contrasting color option in first subparagraph below is sometimes used because it may be difficult to obtain an exact color match between extruded covers and injection-molded end caps and corners.

          - End Caps and Corners:  Prefabricated, injection-molded plastic; matching color   cover; field adjustable for close alignment with snap-on cover.

          - Accessories:  Concealed splices and mounting hardware.

          - Mounting:  Surface mounted directly to wall  .

Retain first paragraph below for less-severe impact conditions than covered in "Crash Rail" Paragraph above.

Rub rails in first paragraph below are often used for wheel protection between crash or bumper rails and the floor.  They are also called "accent rails."

Retain one of first four paragraphs below for protection against scarring by movable furniture.  Revise first paragraph below for products with continuous aluminum retainers for wood rails as well as bumpers, products with more than one bumper strip, or products with bumpers applied directly to wood rails.

If needed, insert requirements for metal for backroom areas with critical sanitary needs and heavy-duty EPDM or natural rubber wall guards for backroom areas subject to industrial-type wheeled traffic.

      - CORNER GUARDS

        - Flush-Mounted, Resilient, Plastic Corner Guards :  Assembly consisting of snap-on plastic cover that is flush with adjacent wall surface, installed over continuous retainer; including mounting hardware; fabricated with 90- or 135-degree turn to match wall condition; full wall height.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following :

          - Basis-of-Design Product:  Subject to compliance with requirements,    or comparable product by one of the following:

            - IPC Door and Wall Protection Systems; Division of InPro Corporation.

            - Korogard Wall Protection Systems; a division of RJF International Corporation.

            - Substitutions:  See Section 01 25 00 – Substitution Procedures.

          - Cover:  Extruded rigid plastic, minimum 0.078-inch (2.0-mm)   wall thickness; as follows:

            - Profile:  Nominal  3-inch- (75-mm-) long leg and 1/4-inch (6-mm) corner radius  .

            - Height:   8 feet (2.4 m) .

            - Color and Texture:    As selected by Architect from manufacturer's full range .

Retain one of first two subparagraphs below.

          - Retainer:  Minimum 0.060-inch- (1.5-mm-) thick, one-piece, extruded aluminum.

          - Retainer Clips:  Manufacturer's standard impact-absorbing clips.

Aluminum cove base in subparagraph below is an optional feature.

      - DOOR PROTECTION SYSTEMS

Retain this article if impact-resistant door protection is required to match impact-resistant wall protection.  Metal armor, kick, mop, and push plates are included in Section 087100 "Door Hardware."

        - General:  Comply with BHMA A156.6.

Only products manufactured by Construction Specialties and InPro are listed in UL's "Fire Resistance Directory."  See Evaluations.

          - For fire-rated doors, provide door protection systems that are UL listed and labeled.

NFPA 80 limits height of protection plates on fire-rated doors to 16 inches (406 mm) above bottom of door unless otherwise specifically labeled.

        - Protection Plates:  Fabricated from extruded rigid plastic, of thickness indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following :

          - Basis-of-Design Product:  Subject to compliance with requirements,    or comparable product by one of the following:

            - IPC Door and Wall Protection Systems; Division of InPro Corporation.

            - Korogard Wall Protection Systems; a division of RJF International Corporation.

            - Substitutions:  See Section 01 25 00 – Substitution Procedures.

Retain first paragraph below if protection of door edges is required.  Door-edge protectors may be used alone or with armor or kick plates for greater protection.  Door edges may need to be undercut to obtain proper edge clearances.

        - Door-Edge Protection :  Fabricated from extruded rigid plastic, minimum 0.040-inch (1.0-mm)   wall thickness; formed to fit over door edge without mortising.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following :

          - Basis-of-Design Product:  Subject to compliance with requirements,    or comparable product by one of the following:

            - IPC Door and Wall Protection Systems; Division of InPro Corporation.

            - Korogard Wall Protection Systems; a division of RJF International Corporation.

            - Substitutions:  See Section 01 25 00 – Substitution Procedures.

          - Shape:  L .

          - Color and Texture:    As selected by Architect from manufacturer's full range .

          - Mounting:   Countersunk screws through factory-drilled mounting holes .

      - FABRICATION

        - Fabricate impact-resistant wall protection units to comply with requirements indicated for design, dimensions, and member sizes, including thicknesses of components.

Construction Specialties is only manufacturer that indicates it can factory fabricate a curved sheet wall covering according to requirements in first paragraph below.  Verify availability with other manufacturers.

        - Preform curved semirigid, impact-resistant sheet wall covering in factory for radius and sheet thickness as follows:

          - Sheet Thickness of 0.040 Inch (1.0 mm):  24-inch (610-mm) radius.

        - Assemble components in factory to greatest extent possible to minimize field assembly.  Disassemble only as necessary for shipping and handling.

        - Fabricate components with tight seams and joints with exposed edges rolled.  Provide surfaces free of wrinkles, chips, dents, uneven coloration, and other imperfections.  Fabricate members and fittings to produce flush, smooth, and rigid hairline joints.

        - Miter corners and ends of wood handrails for returns.

      - METAL FINISHES

Retain this article only for metal corner guards.

        - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

          - Remove tool and die marks and stretch lines, or blend into finish.

          - Grind and polish surfaces to produce uniform finish, free of cross scratches.

Retain first subparagraph below for directional finishes.

          - Run grain of directional finishes with long dimension of each piece.

          - When polishing is completed, passivate and rinse surfaces.  Remove embedded foreign matter and leave surfaces chemically clean.

        - Protect finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

- EXECUTION

      - EXAMINATION

        - Examine substrates and wall areas, with Installer present, for compliance with requirements for installation tolerances[, fire rating,] and other conditions affecting performance of work.

        - Examine walls to which impact-resistant wall protection will be attached for blocking, grounds, and other solid backing that have been installed in the locations required for secure attachment of support fasteners.

          - For impact-resistant wall protection units attached with adhesive or foam tape, verify compatibility with and suitability of substrates, including compatibility with existing finishes or primers.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Complete finishing operations, including painting, before installing impact-resistant wall protection system components.

        - Before installation, clean substrate to remove dust, debris, and loose particles.

      - INSTALLATION

        - General:  Install impact-resistant wall protection units level, plumb, and true to line without distortions.  Do not use materials with chips, cracks, voids, stains, or other defects that might be visible in the finished Work.

          - Install impact-resistant wall protection units in locations and at mounting heights indicated on Drawings or, if not indicated, at heights indicated below:

            - Crash Rails:  <Insert dimension> above finished floor.

            - Bumper Rails:  <Insert dimension> above finished floor.

            - Rub Rails:  <Insert dimension> above finished floor.

            - Chair Rails:  <Insert dimension> above finished floor.

            - Handrails:  <Insert dimension> above finished floor.

            - Bed Locators:  <Insert dimension> above finished floor.

            - <Insert product and location>.

          - Provide splices, mounting hardware, anchors, and other accessories required for a complete installation.

            - Provide anchoring devices to withstand imposed loads.

            - Where splices occur in horizontal runs of more than 20 feet (6.1 m), splice aluminum retainers and plastic covers at different locations along the run, but no closer than 12 inches (305 mm).

            - Adjust [end] [and] [top] caps as required to ensure tight seams.

        - Impact-Resistant Wall Covering:  Install top and edge moldings, corners, and divider bars as required for a complete installation.

      - CLEANING

        - Immediately after completion of installation, clean plastic covers and accessories using a standard, ammonia-based, household cleaning agent.

Retain paragraph below if using adhesive.

        - Remove excess adhesive using methods and materials recommended in writing by manufacturer.

END OF SECTION 10 26 00